## HVAC
Cooling Cost Comparison
|  |  | AOS | OSF
Number of Years |  |  | 20 | 20
Capital cost |  |  | 163636.5679 | 158636.5679 | Note 1
Maintenance Cost |  |  | 44056.0114 | 44056.0114 |  |  | operating plus maintenance:
Operating Costs |  |  | 1145456.2965 | 2202800.5702 |  |  | 1189512.3079 | 2246856.5816
Total 20-year cost |  |  | 1353148.8758 | 2405493.1495
Cost savings over 20 years: |  |  | 1052344.2737 | -1052344.2737
Conclusion: Cooling at AOS saves significant dollars due to operational savings due to use of ambient cooling
Background information:
Based on current weather
location | hPA | in mercury | ratios relative to sea level | ratios relative to AOS
AOS | 556 | 16.41 | 0.54941 | 1 |  | 1.8201
OSF | 722 | 21.32 | 0.71344 | 1.2986 |  | 1.4017
VA Beach | 1012 | 29.87 | 1 | 1.8201 |  | 1
based on graphs from wikipedia
density ratio at 5000 meters = 0.6 + (2/44)0.1 = .605
density ratio at 3000 meters = 0.7 + (18/44)0.1 = .741
ratio of densities @ 3000 m and 5000 m = .741/0.605 = 1.225
pressure ratio at 5000 meters = 0.5 + (15/48)0.1 = .53
pressure ratio at 3000 meters = 0.6 + (43/48)0.1 = .690
ratio of pressures @ 3000 m and 5000 m = .690/0.530 = 1.30 (very close to above from pressure readings on 6/15/2016)
From [1]
| Internal load | 170 | KW
| Required Safety Factor | 1.2
| Altitude | 5075 | m
| Barometric Pressure | 58.9 | % of sea level
| Desired Room Air Temperature | 20 | degrees C
Q = mfr Cp DT
= 1.085 cfm DT
where
Q = heat loss/gain (kw)
mfr = mass flow rate, kg/hr
D= supply air temperature minus return air temperature
cfm = cubic feet per minute
Q = 685,000 Btuh = 1.085 cfm (68 - 52)oF
At 5075m
cfm = 39,500/0.0589 = 67,000 cfm (31,620 l/s)
The intent is to use two air handlers, each capable of supplying 33,500 cfm (15,810 l/s)
From [2]
Use of an "economizer" saves money at AOS, not possible at OSF
| At AOS: | "Option 2" | "Option 5" | "Option 6"
| Capital cost | 83000 | 115000 | 91000
| Annual Maintenance cost | 2000 | 2500 | 1500
| Annual Operating cost | 88000 | 56000 | 39000
At OSF
| Capital cost | 83000 | not doable | 91000
| Annual Maintenance cost | 2000 |  | 1500
| Annual Operating cost | 88000 |  | 75000
According to chiller manufacturers, any equipment derating for the chiller condenser fans are largely offset by the gain received from the lower ambient temperatures
In actuality, the lower site will require slightly less airflow and therefore the costs will be slightly less, possibly $1,000 to $2,000 per air handler.
Freight, taxes and import duties not included in above
| cost per kw-hr | kw | hr | yearly cost
| 0.1 | 170 | 8760 | 148920
| 0.05 | 170 | 8760 | 74460 | M3 probably assumed $0.05 per kw-hr
| 0.3 | 170 | 8760 | 446760 | real cost at 30 cents per kw-hr
|  |  |  | 6 | operatingCostCorrectionFactor
inflation factor
| per cent per year | 3
| number of years | 13
| inflation factor | 1.4685
freight, taxes, import, installation
| AOS | 30000 |  |  | estimate based on correlator shipping and installation
| OSF | 25000
[1] | Correlator Room AC Calculation.pdf, M3 Engineering Technology Corp., Oct 24, 2003 available on EDM at http://edm.alma.cl/forums/alma/dispatch.cgi/ipt20docs/docProfile/100301/
[2] | Correlator Room HVAC Study, STE-20.01.02.00-002-A-REP.pdf, on EDM at http://edm.alma.cl/forums/alma/dispatch.cgi/ipt20docs/docProfile/100073/

## People Transport
Costs associated with travel to the AOS to service the correlator
| Number of FTEs required to go to AOS to service the correlator | 2
| time wasted/FTE on a trip to the AOS1 | 2
| Time wasted/trip: | 4 | hrs
| Number of trips/yr 2 | 52
| Number of years | 20 |  | 1190
| Hours wasted | 4160 |  | 400
| Number of working hours per year per FTE | 2080 |  | 62
| Fraction of FTE time wasted | 0.05 |  | 37
| Cost of FTE-year | 200000 |  | 1689
| Dollar cost of hours wasted per FTE per year | 10000
| Wasted labor over 20 years | 400000
| Number of km driven per trip | 60 | km
| Cost of vehicle operation per km | 1 | should try to get a better estimate
| Vehicle cost over 20 years | 62400
| Cost of high-altitude bonus per person per trip 2 | 18
| Number of people required per trip | 2
| Cost of high-altitude bonus over 20 years | 37440
| Total incremental personnel cost over 20 years | 499840
Notes:
1 - Includes driving time and time loading and unloading the vehicle
2 - Source is Alejandro Saez

## Science Time
"Productivity" costs of lost science with the correlator housed at the AOS
| Capital cost of ALMA | 1500000000
| Operating cost per year | 50000000
| Lifetime of ALMA | 30 | years
| 30-year operating costs | 1500000000
| Total ALMA cost for 30 yr | 3000000000
| Cost per year1 | 100000000
| Hours per year | 8766
| Cost per hour | 11407.7116
| Number of maintenance trips to the AOS per year | 52
| Hours of science time lost per trip, day | 2
| Hours of science time lost per trip, night | 8
| Mean hours lost per trip | 5
| Science hours lost per year | 260
| Number of years | 20
| Science time lost over number of years | 5200
| Value of lost science for Case 2 | 59320100.3879
Time lost during transition period for AOS existing room
| #days | 60 | estimate based on past experience
| mean fraction of days normally used for science | 0.6 | guess
| total hours lost during transition | 864
| cost of science time lost for Case 1 | 69176363.2215

## Room
Costs of space for correlator and HVAC for Cases 2 and 4
Need space for 11 racks
Need space to work around racks
Need space for HVAC |  |  | metric equivalent |  |  | OSF room costs breakdown
|  |  | 0.093 | square meters per square foot |  | Correlator | 129960
Square feet/rack | 7.0486 |  | 0.65552 |  |  | HVAC | 577600
Square feet/11 racks1 | 90 | sq-ft | 8.37
Working space | 270 | sq-ft | 25.11
space for HVAC | 1600 |  | 148.8 |  | source: existing HVAC is about the size of the existing correlator room
Total | 1967.0486 |  | 182.9355
cost of construction
AOS (correlator space) | 673 | $/sq-ft | 62.589 |  | source: Jason Jennings, private communication, see below; average cost per square foot of AOS
AOS(HVAC space) | 673 | $/sq-ft |  |  | Perhaps this space can be less expensive?
OSF (correlator space) | 361 | $/sq-ft | 33.573 |  | From Jason Jennings: $38.8M/10,000 m^2 => $361/ft^2
OSF (HVAC space) | 361 | $/sq-ft |  |  | Perhaps this space can be less expensive?
college laboratory, US avg | 200 | $/sq-ft | 18.6 |  | source: BuildingJournal.com
AOS total | 1319080 |  |  |  | both seem high. Space for HVAC drives the cost. Cheaper space for HVAC?
OSF total | 707560
Notes:
1 - 8 racks for the correlator proper (source: Carlson), 2 rack for computers and networking, 1 rack for fiber demultiplexing
2 - rack mount ("earthquake mount")is called out separately
3 - HVAC is costed separately
Jason Jennings info:
Subject:
RE: ALMA costs
From:
Jason Jennings <jjenning@nrao.edu>
Date:
2016-07-22 16:58
To:
Rich Lacasse <rlacasse@nrao.edu>
CC:
William Randolph <wrandolp@nrao.edu>
Hi Rich,
Bill and I have been looking into this, and have reached out to some folks at JAO and the AUI Office and we this is what have found in the records:
AOS was approx. $11.1M from back around 2009, so at 1.5% inflation that bring you up to around $12.3M in 2016.
Total SqFt of AOS is ~18.3k, so you are looking at $673 per sqft at AOS
OSF was 25.0M EUR, so at 1.4 $/EUR (back then) that comes up to $35M USD. With 1.5% escalation we are up to $38.8M in 2016.
I don’t have info on square footage for this at this point, but we have requested that info. I will let you know as soon as I hear.
Please let me know if you have questions. Thanks.
- Jason

## Data Transport
Cost of transporting current data to OSF in 2016 dollars
Desc. | Qty | Unit cost | total cost
2:1 splitters | 55 | 95 | 5225 | source OEQuest.com
4:1 splitters | 18 | 140 | 2520 | source OEQuest.com
DWDM | 18 | 8700 | 156600 | source: Doeleman
transceivers (in packaged modules) | 880 | 1150 | 1012000 | source: http://www.fs.com/dwdm-sfp-plus-transceivers-sid-191.html
receivers (on daughter cards in correlator) | 880 | 150 | 132000 | source: various
cables | 150 | 150 | 22500 | source: guestimate
racks and misc | 1 | 50000 | 50000 | source: guestimate
Installation/test (4 weeks, 2 FTE) | 1 | 12000 | 12000 | source: guestimate
Design, Assemble, Document, PAI | 1 | 250000 | 250000 | 0.5 FTE year
Travel | 2 | 5000 | 10000
Contingency (10%) | 1 |  | 165284.5
Total |  |  | 1818129.5
Big assumption: Space for this is available at both AOS and OSF
Big question: what to do about transceiver spares?
Note: In the 2022 time frame these costs will go down. Chris Jacques estimates decrease of about 30%
Cost of transport 4x BW and 4 bits in year 2022
Assumption: In 2022, 40 Gb/s tranceivers should be available for the present cost of 10 Gb/s transceivers
The requirement to transmit 4 bits instead of 3 will increase the cost by ~4/3
For the final estimate, simply multiply the above estimate by 4/3
Estimated Cost: |  |  | 2424172.6667

## change log
Date | Change
2016-08-17 | Update OSF cost per Jason Jennings email ($361/sq-ft for OSF)